## Slide 1: LINEAR DRAIN SYSTEMS:
DESIGN, INSTALLATION, & APPLICATION

## Slide 2: Course Outline: 1 hour AIA CEU “Health, Safety, and Welfare Credit”
Traditional & Modern types of waterproofing within an indoor wet area and/or bathroom.
How to design a “Barrier Free Bathroom” using Linear Drain Systems.
Floor Pitch & ADA requirements within the indoor wet area/bathroom.
Outdoor Architectural trench drain design and applications.

## Slide 3: Traditional Shower Drain

## Slide 4: Linear Drains
Slope the floor in one direction towards the drain
Use large format tile, stone slab or solid surface material
Create a barrier-free or curbless shower
Drain is now a design element

## Slide 5: How Do I Choose?
Which one do I like?
Which one do I need?

## Slide 6: Decorative Top Grates

## Slide 7: Traditional Waterproofing
Lead Pan
PVC Vinyl
CPE
Hot Mop
Notes: These methods require multiple levels of installation, skill set, and limited square footage. They also use a clamp down method water in/water out drain system.
The traditional method for installing tiled shower assemblies begins with the installation of a mortar bed that is sloped to the weep holes in the drain. A waterproofing membrane, typically referred to as a pan liner, is subsequently placed over this "pre-slope" and clamped into the drain. Pan liners may consist of metals such as lead and copper or plastics such as polyvinyl chloride (PVC) and chlorinated polyethylene (CPE). Some regions of the country also employ hot mop systems that involve applying layers of asphalt and roofing felt to build up a pan liner. Pan liners are carried up to a height of at least 3" above the finished height of the curb, and must not be penetrated by any fasteners. Pan liners are not designed to allow for the direct application of ceramic or stone tile. Thus, a mortar bed must be installed to provide load distribution and a bonding surface for the floor tile. Crushed stone or tile is placed around the weep holes of the drain to prevent blockage before installing the mortar bed. Most wall assemblies incorporate 4-mil polyethylene or roofing felt placed behind the tile substrate (i.e., floated mortar or backerboard panels) and lapped over the pan liner.

## Slide 8: Site Sizable Linear Drain Systems
Standard USA Install
Modify length of grate and channel on-site to exact specifications
Place outlet anywhere along channel run
Channel in Stainless Steel or PVC
Neutral pitch channel
Components can be combined for form any length.

## Slide 9: Site Sizeable Clamping Flange – PVC Against the Wall

## Slide 10: Site Sizeable Clamping Flange – All Stainless, Against the Wall

## Slide 11: Fixed Length Linear Drain Systems
Fixed Length grate and channel
Set center outlet location
Pre-pitched channel
Stainless steel grate and channel
Custom sizing available
Challenges in wall-to-wall installation

## Slide 12: Fixed Length Clamping Flange – Straight Edge Channel, Zero-Threshold

## Slide 13: Modern Waterproofing No-Hub Connection
Fabric Sheet
Schluter – Kerdi Adheres to the substrate with thin-set mortar or other adhesive. Allows for direct application of tile
Liquid Membrane
Laticrete – Hydro Ban “Paint on” waterproofing allows for direct application of tile
Easily waterproof the entire bathroom

## Slide 14: Fixed Length Direct Connect – Flanged Channel, Against the Wall

## Slide 15: Recommended Drain Placement

## Slide 16: Recommended Drain Placement

## Slide 17: Recommended Drain Placement

## Slide 18: Recommended Drain Placement

## Slide 19: Floor pitch and ADA requirements
Transfer Type Shower Compartments
Standard Roll-In Type Shower Compartments
Alternate Roll-In Type Shower Compartments

## Slide 20: Transfer Type Shower compartments
Dimensions
      36” x 36” clear inside dimensions,
      36” wide entry
      36” x 48” clearance to entry
Only configuration that allows a curb
FIGURE 608.2.1
Per ADA 608.2.1, 608.7 & 303
Notes: Clearance of 36 inches (915 mm) wide minimum by 48 inches (1220 mm) long minimum measured from the control wall shall be provided.
Exception of existing facility where 1/2” threshold would disturb structural reinforcement of slab.

## Slide 21: Standard Roll-In Type Shower compartments
Dimensions
30” x 60” clear inside dimensions
60” wide entry
30’ x 60” clearance to entry
Exception of lav on one 30” clearance if not by controls or shower seat
Thresholds - 1/2” (13mm) high max
FIGURE 608.2.2
Per ADA 608.2.2, 608.2.2.1, 608.7 & 303
Notes: 608.2.2.1 Clearance. A 30 inch (760 mm) wide minimum by 60 inch (1525 mm) long minimum clearance shall be provided adjacent to the open face of the shower compartment.

## Slide 22: Alternate Roll-In Type Shower Compartments
FIGURE 608.2.3
Dimensions
36” x 60” clear inside dimensions
36” wide entry along long side
Thresholds in roll-in type shower compartments shall be ½“ high max
Per ADA 608.2.2, 608.2.2.1, 608.7 & 303
Notes: 608.2.2.1 Clearance. A 30 inch (760 mm) wide minimum by 60 inch (1525 mm) long minimum clearance shall be provided adjacent to the open face of the shower compartment.

## Slide 23: Open Shower

## Slide 24: Outdoor Architectural Trench Drains
design & application

## Slide 25: Storm Drainage & Landscape

## Slide 26: Driveways

## Slide 27: Balconies

## Slide 28: Patio & Deck

## Slide 29: Pool Surrounds
Use as a wet edge pool detail

## Slide 30: Questions?